## Overview
Content | Nuclear technology parameters
Part of | GG-SMR project T5.3
Author | Topi Rasku <topi.rasku@vtt.fi>
Last updated | 2025-09-10
Description | This dataset contains more detailed nuclear technology parameters focusing on light-water reactors (LWRs) both conventional as well as micro- and small modular reactors (SMRs) for power and heat generation.
Note that this is not a standalone input data file and requires the other North European model dataset as a basis.
E.g. for the `unittype`s to appear in the final processed input data, you need to provide some scenario `unitdata` for the processing.
See the later "Discussion" for justification on selected input data focus, as well as some caveats.
The data is organized into 5 scenarios sampling data differently across the sources. Note that in e.g. "nucLow", all parameters are low: both technical and economical!
nucMin - Contains extreme low-end (i.e. minimum) parameters. Likely highly unrealistic, not recommended for actual use, but included for completeness' sake.
nucLow - Contains low-end parameters supposedly within the realm of possibility. Sample these if you feel like using conservative technical parameters or optimistic cost assumptions.
nucTypical - Contains "middle-of-the-pack" parameters aiming to represent expected parameters. This scenario could be used as-is.
nucHigh - Contains high-end parameters within the realm of possibility. Sample these if you want to use optimistic technical parameters or conservative cost assumptions.
nucMax - Contains extreme high-end (i.e. maximum) parameters. Not recommended for actual use and included primarily for completeness' sake.
The unit type data is categorized via two "axes":
LRW-SMLRW-MMLRW: Indicates whether the unit is a large LWR (~1000 MWe), a Small Modular LWR (<300 MWe), or a Micro Modular LWR (<50 MWth).
CHP-DH: Indicates whether the unit is a Combined Heat and Power or a District Heat-Only unit. If not indicated, the unit is electricity only.
Note that the investment costs don't cover power or district heating grid connection costs: E.g. a "Conventional LWR CHP" unit would likely require quite an atypical district heating connection due to its size and presumed distance from any urban areas.
Note that this dataset is not methodologically rigorous.
Parameter selection was largely based on subjective estimation of source credibility, not on any well-defined meta-analysis.
Furthermore, currencies and their respective exchange rates or their evolution were not rigorously accounted for.
Regardless, the considerable range of uncertainty in the parameters renders this dataset more informative than anything else.
Data quality on the data sheets is indicated using the following colors:
| Good | Data could be easily based on listed sources with multiple alternatives available for comparison
| Decent | Data could be based on listed sources, but limited or no alternatives were available for comparison, or was used slightly outside its original intended purpose.
| Bad | Data could not be based to listed sources, and subjective guesstimation from undocumented legacy data or arbitrary extrapolation was used as a supplement.
| Derived | Derived from other data values.
Key sheets
sources | Contains the raw data table from my original parameter gathering while delving into SMR literature.
unittypedata | Contains the technology parameters for different nuclear technologies.
Discussion | The focus of this dataset is on emerging light-water micro- and small modular reactors, as well as modern conventional nuclear power plant (NPP) designs.
Thus, the parameters aim to reflect the properties of "Gen III+" Light Water Reactors (mainly Pressurized Water Reactor, not Boiling Water Reactor).
The main reason for this are:
1. LWR and especially PWR reactors constitute the majority of existing NPPs.
2. Small modular LWRs are technologically more mature than alternative (Gen IV) designs, and thus likely to be commercialized first.
3. Parameters are more plentiful and reliable due to existing experience with large LWRs, and we don't need to rely on design-specific developer-advertised values.
4. All mature LWR designs use Low-Enriched Uranium (LEU ~3-5% U235) fuel, whereas some Gen IV SMR designs require High-Assay LEU (HALEU ~5-20% U235), the global supply of which is much more scarce.
However, it should be noted that this limits the applicability of the output heat, as LWRs are generally only capable of max 300C heat output.
This makes them suitable for district heating, desalination, and some pulp & paper processes, but not enough for a lot of other industrial processes or high-temperature hydrogen electrolysis.
Gen IV reactors would be required for process heat in the 300-900C ranges, but those are likely decades away from commercial deployment.
The main uncontested advantage of SMRs is their ability (if permitted) to operate where large NPPs cannot: isolated/maritime/mobile environments, or close to urban and industrial areas for efficient co-generation.
However, SMRs still face significant uncertainties in their deployment:
1. Their technology is still unproven and economics uncertain (especially for Gen IV designs).
Whether mass production of modularized SMRs can recoup lost economies of scale remains uncertain, as SMR factories are massive upfront investments.
In principle, financing costs and risks should be lower than in conventional "megaprojects" due to shorter and modular construction times.
Economic competitiveness with VRE also often called into question for pure power production (outside supplying specific steady consumers outside wholesale markets).
2. Nuclear safety regulations and nuclear proliferation concerns need to be sorted out (again worse for Gen IV due to potentially higher enriched fuel).
SMR safety needs to be evaluated differently than traditional power plants, especially if situated in urban or industrial areas for co-generation, complicating regulatory approval processes.
More spread out nuclear material raises concerns about security and proliferation risks for SMRs.
Overall, there is surprisingly little difference in SMR and NPP parameters for power generation, nor does there seem to be good reasons to expect otherwise.
LWR reactors capable of temperatures required for "efficient" power generation are conceptually similar regardless of their size.
What SMRs could save in mass production, they seem to lose in economies of scale (the massive upfront costs of "SMR factories" are a key economic uncertainty).
However, low-temperature heat-only reactors likely have significantly lower costs due to simplified design, which is at least somewhat reflected in the parameters.
The flexible operation parameters are possibly partially better for SMRs, but concrete data on this is limited.
Based on the literature, the phenomena limiting reactor flexibility seem to relate to:
1. Minimum load avoids issues with xenon transients and soluble boron concentrations throughout the fuel cycle.
Likely to impact all LWR reactors somewhat equally regardless of their size.
Early in the fuel cycle, load-following between 20-100% is technically feasible under modern reactor reactivity requirements, but the last third of the cycle gradually becomes completely inflexible.
40-50% min load often considered a decent average for simpler modelling purposes.
Low-temperature heat-only reactors might differ in terms of xenon transients and soluble boron utilisation, yielding different minimum loads, but I would have to consult reactor dynamics specialists on the topic.
2. Startup/shutdown durations seem to be governed by the time it takes for the reactor core to safely heat up and cool, although thermal stress as well as xenon transients can still play a part depending on the fuel cycle.
Thus, this time could be noticeably lower for SMRs with smaller cores that should be faster to cool and heat up evenly, unless thermal stresses become an issue (which they shouldn't based on ramping capabilities?).
There is a huge difference between "hot" and "cold" startups for nuclear reactors depending on the temperature of the reactor, the primary cooling circuit, and the turbine.
A "hot-hot" startup after less than 36 hours of "hot-shutdown-mode" only takes ~2 hours, while a "cold-cold" startup after e.g. a refuelling outage takes ~40 hours.
In principle, startup and shutdown numbers for NPPs over the lifetime are also limited to minimize thermal/corrosive stress on the reactor core (~20 hot starts per year, ~1-2 cold starts per year), but how these apply to SMRs is unknown.
Low-temperature heat-only reactors might require even less time due to small size and already lower core temperatures.
3. Ramp limits are in place to minimize thermal stress on fuel assemblies and minize risk of fuel rod rupture.
As such, ramp limits are likely similar for NPPs and SMRs regardless of their size.
Modern reactors should be capable of at least 3%/min in regular operation, and while TSOs can require more, 5%/min is a currently agreed-upon hard safety cap.
Technically modern reactors should also be capable of ramping down at 20%/min, but this is reserved for emergencies.
NPPs should technically be capable of ramping between full-min-full power cycles: 2x per day, 5x per week, or 200x per year.
However, low-temperature heat-only reactors might again be capable of faster ramping due to lower temperatures and thus fuel rod thermal stress?

## sources
Stars indicate priority sources
e = electricity only, chp = combined heat and power, ho = heat-only
Table source: <topi.rasku@vtt.fi> GG-SMR working draft
Last updated: 2025-08-25
Priority | [1] C. Bruynooghe, A. Eriksson, and G. Fulli, “Load-following Operating Mode at Nuclear Power
Plants (NPPs) and Incidence on Operation and Maintenance (O&M) Costs — Compatibility
with Wind Power Variability,” Tech. Rep. EUR 245834 EN - 2010, European Commission
Joint Research Centre Institute for Energy, Luxembourg, 2010. ISBN: 9789279175343 ISSN:
1018-5593.
[2] G. Simbolotti, “IEA ETSAP — Technology Brief E03 – Nuclear Power,” Apr. 2010.
[3] Nuclear Energy Agency, “Technical and Economic Aspects of Load Following with Nuclear
Power Plants,” tech. rep., Nuclear Energy Agency, June 2011.
Priority | [4] EUR Association, “Chapter 2 — Performance requirements,” in European utility requirements
for LWR nuclear power plants, vol. 2, EUR Association, revision e ed., Dec. 2016.
[5] C. Cany, C. Mansilla, P. da Costa, G. Mathonni`ere, T. Duquesnoy, and A. Baschwitz, “Nuclear
and intermittent renewables: Two compatible supply options? The case of the French power
mix,” Energy Policy, vol. 95, pp. 135–146, Aug. 2016.
[6] V. Tulkki, E. Pursiheimo, and T. J. Lindroos, District heat with Small Modular Reactors
(SMR). VTT Technical Research Centre of Finland, 2017.
Priority | [7] International Atomic Energy Agency, “Non-baseload Operation in Nuclear Power Plants: Load
Following and Frequency Control Modes of Flexible Operation,” text, International Atomic
Energy Agency, Apr. 2018. ISBN: 9789201108166 Publication Title: Non-baseload Operation
in Nuclear Power Plants: Load Following and Frequency Control Modes of Flexible Operation.
[8] K. V¨arri and S. Syri, “The Possible Role of Modular Nuclear Reactors in District Heating:
Case Helsinki Region,” Energies, vol. 12, p. 2195, June 2019. Number: 11 Publisher: Multi-
disciplinary Digital Publishing Institute.
[9] M. Nichol and H. Desai, “Cost Competitiveness of Micro-Reactors for Remote Markets,” tech.
rep., Nuclear Energy Institute, Apr. 2019.
Priority | [10] T. J. Lindroos, E. Pursiheimo, V. Sahlberg, and V. Tulkki, “A techno-economic assessment of
NuScale and DHR-400 reactors in a district heating and cooling grid,” Energy Sources, Part
B: Economics, Planning and Policy, vol. 14, pp. 13–24, Mar. 2019.
[11] Nuclear Energy Agency, “The Costs of Decarbonisation: System Costs with High Shares of
Nuclear and Renewables,” Tech. Rep. 7299, Nuclear Energy Agency, 2019.
[12] V. Nian and S. Zhong, “Economic feasibility of flexible energy productions by small modular
reactors from the perspective of integrated planning,” Progress in Nuclear Energy, vol. 118,
p. 103106, Jan. 2020.
[13] A. Ter¨asvirta, S. Syri, and P. Hiltunen, “Small Nuclear Reactor—Nordic District Heating Case
Study,” Energies, vol. 13, p. 3782, July 2020. Number: 15 Publisher: Multidisciplinary Digital
Publishing Institute.
[14] R. Testoni, A. Bersano, and S. Segantin, “Review of nuclear microreactors: Status, potential-
ities and challenges,” Progress in Nuclear Energy, vol. 138, p. 103822, Aug. 2021.
[15] Nuclear Energy Agency, “Small Modular Reactors: Challenges and Opportunities,” Tech. Rep.
7560, Nuclear Energy Agency, 2021.
[16] A. Lynch, Y. Perez, S. Gabriel, and G. Mathonniere, “Nuclear fleet flexibility: Modeling and
impacts on power systems with renewable energy,” Applied Energy, vol. 314, p. 118903, May
2022
[17] E. Pursiheimo, T. J. Lindroos, D. Sundell, M. R¨am¨a, and V. Tulkki, “Optimal investment
analysis for heat pumps and nuclear heat in decarbonised Helsinki metropolitan district heating
system,” Energy Storage and Saving, vol. 1, pp. 80–92, June 2022.
[18] G. Black, D. Shropshire, K. Ara´ujo, and A. van Heek, “Prospects for Nuclear Microre-
actors: A Review of the Technology, Economics, and Regulatory Considerations,” Nu-
clear Technology, vol. 209, pp. S1–S20, Jan. 2023. Publisher: Taylor & Francis eprint:
https://doi.org/10.1080/00295450.2022.2118626.
[19] S. Alhadhrami, G. J. Soto, and B. Lindley, “Dispatch analysis of flexible power operation with
multi-unit small modular reactors,” Energy, vol. 280, p. 128107, Oct. 2023.
[20] A. Asuega, B. J. Limb, and J. C. Quinn, “Techno-economic analysis of advanced small modular
nuclear reactors,” Applied Energy, vol. 334, p. 120669, Mar. 2023.
[21] A. Rigby, S. Alhadhrami, and B. Lindley, “Co-optimization of nuclear reactor flexible power
operation and maintenance scheduling,” Energy, vol. 313, p. 134098, Dec. 2024.
[22] L. Sokka, H. Kirppu, and J. Lepp¨anen, “Evaluation of Life Cycle CO2 Emissions for the LDR-
50 Nuclear District Heating Reactor,” Energies, vol. 17, p. 3250, July 2024. Number: 13
Publisher: Multidisciplinary Digital Publishing Institute.
Priority | [23] N. Van Hee, H. Peremans, and P. Nimmegeers, “Economic potential and barriers of small
modular reactors in Europe,” Renewable and Sustainable Energy Reviews, vol. 203, p. 114743,
Oct. 2024.
[24] C. Kost, P. M¨uller, J. S. Schweiger, V. Fluri, and J. Thomsen, “Study: Levelized Cost of Elec-
tricity — Renewable Energy Technologies,” tech. rep., Fraunhofer Institute for Solar Energy
Systems, Freiburg, June 2024.
Priority | [25] A. Abou-Jaoude, C. S. Lohse, L. M. Larsen, N. Guaita, I. Trivedi, F. C. Joseck, E. Hoffman,
N. Stauff, K. Shirvan, and A. Stein, “Meta-Analysis of Advanced Nuclear Reactor Cost Es-
timations,” Tech. Rep. INL/RPT–24-77048-Rev001, Idaho National Laboratory (INL), Idaho
Falls, ID (United States), June 2024.
Priority | [26] NREL (National Renewable Energy Laboratory), “2024 Annual Technology Baseline,” July
2024
Priority | [27] ENTSO-E, “ERAA 2024 Downloads,” 2024.
[28] J. Rahman and J. Zhang, “Steady-State Modeling of Small Modular Reactors for Multi-
Timescale Power System Operations With Temporally Coupled Sub-Models,” IEEE Trans-
actions on Power Systems, vol. 40, pp. 793–805, Jan. 2025.
[29] M. Hjelmeland, J. K. Nøland, S. Backe, and M. Korp˚as, “The role of nuclear energy and
baseload demand in capacity expansion planning for low-carbon power systems,” Applied En-
ergy, vol. 377, p. 124366, Jan. 2025.
[30] C. K. Simoglou, I. M. Kaissas, and P. N. Biskas, “Assessing the Implications of Integrating
Small Modular Reactors in Modern Power Systems,” Energies, vol. 18, p. 2578, May 2025.
Publisher: Multidisciplinary Digital Publishing Institute.
[31] A. I. Arvanitidis and M. Alamaniotis, “Optimal Economic Dispatch and Load-Following Strate-
gies for Nuclear Integrated Energy Systems,” IEEE Access, vol. 13, pp. 118857–118873, July
2025
[32] “Lazard LCOE+,” June 2025.
Priority | [33] J.-P. Ikonen, T. J. Lindroos, and P. Hiltunen, “Feasibility of small modular reactors for de-
carbonizing district heating systems: a case study of the Helsinki metropolitan area,” Nuclear
Engineering and Design, vol. 442, p. 114262, Oct. 2025.

## unittypedata
scenario | year | Generator_ID | unittype | isSource | isSink | flow | LP/MIP | emission_group1 | grid_input1 | grid_output1 | grid_output2 | conversionCoeff_output2 | grid_output3 | eff00 | eff01 | op00 | op01 | cb | cv | vomCosts | vomCosts_input1 | minOperationHours | minShutDownHours | startfuelConsWarm | startCostWarm | startFuelConsCold | startCostCold | startFuelConsHot | startCostHot | startWarmAfterXHours | startColdAfterXhours | maxRampUp | maxRampDown | unitSize | rampUpCost | upperLimitCapacityRatio_input1 | useTimeseriesAvailability | fomCosts | invCosts | annuityFactor | Technical lifetime | Discount rate | CHP cost surcharge | EUR/USD assumed conversion | Note
nucMin | 1 | Conventional LWR | nuclearLWR | [5 empty] | Nuclear | elec |  |  |  | 0.31 | 0.31 | 0.2 | 1 |  |  | 1.2 |  | 2 | 2 | 1.95 | 5 | 3.89 | 300 | 0.98 | 2.5 | 36 | 144 | 0.005 | 0.005 | 300 | 300 |  |  | 90000 | 1530000 | 0.075009 | 40 | 0.07 |  | 0.9
nucLow | 1 | Conventional LWR | nuclearLWR | [5 empty] | Nuclear | elec |  |  |  | 0.32 | 0.32 | 0.4 | 1 |  |  | 1.9 |  | 6 | 10 | 1.95 | 11 | 3.89 | 400 | 0.98 | 5.5 | 36 | 144 | 0.01 | 0.01 | 600 | 400 |  |  | 113400 | 2025000 | 0.07246 | 50 | 0.07 |  | 0.9
nucTypical | 1 | Conventional LWR | nuclearLWR | [5 empty] | Nuclear | elec |  |  |  | 0.33 | 0.33 | 0.5 | 1 |  |  | 2.8 |  | 8 | 24 | 1.95 | 21 | 3.89 | 500 | 0.98 | 10.5 | 36 | 144 | 0.03 | 0.03 | 1000 | 500 |  |  | 157500 | 4275000 | 0.071229 | 60 | 0.07 |  | 0.9 | Uses 0.9 EUR/USD average conversion rate between 2020-2025
nucHigh | 1 | Conventional LWR | nuclearLWR | [5 empty] | Nuclear | elec |  |  |  | 0.34 | 0.34 | 0.8 | 1 |  |  | 3.4 |  | 12 | 40 | 1.95 | 31 | 3.89 | 600 | 0.98 | 15.5 | 36 | 144 | 0.05 | 0.05 | 1300 | 600 |  |  | 183600 | 6975000 | 0.07062 | 70 | 0.07 |  | 0.9
nucMax | 1 | Conventional LWR | nuclearLWR | [5 empty] | Nuclear | elec |  |  |  | 0.36 | 0.36 | 0.95 | 1 |  |  | 16.4 |  | 96 | 96 | 1.95 | 100 | 3.89 | 2000 | 0.98 | 50 | 36 | 144 | 0.1 | 0.2 | 1750 | 2000 |  |  | 207000 | 14400000 | 0.070314 | 80 | 0.07 |  | 0.9
nucMin | 1 | Conventional LWR CHP | nuclearLWRchp | [5 empty] | Nuclear | elec | dheat |  |  | 0.61 | 0.61 | 0.2 | 1 | 0.2 | -0.17 | 1.2 |  | 2 | 2 | 1.95 | 5 | 3.89 | 300 | 0.98 | 2.5 | 36 | 144 | 0.005 | 0.005 | 300 | 300 |  |  | 90000 | 1530000 | 0.075009 | 40 | 0.07 | 1
nucLow | 1 | Conventional LWR CHP | nuclearLWRchp | [5 empty] | Nuclear | elec | dheat |  |  | 0.81 | 0.81 | 0.4 | 1 | 0.3 | -0.16 | 2.01 |  | 6 | 10 | 1.95 | 11.66 | 3.89 | 424 | 0.98 | 5.83 | 36 | 144 | 0.01 | 0.01 | 600 | 424 |  |  | 120204 | 2146500 | 0.07246 | 50 | 0.07 | 1.06
nucTypical | 1 | Conventional LWR CHP | nuclearLWRchp | [5 empty] | Nuclear | elec | dheat |  |  | 0.875 | 0.875 | 0.5 | 1 | 0.4 | -0.15 | 3.11 |  | 8 | 24 | 1.95 | 23.31 | 3.89 | 555 | 0.98 | 11.66 | 36 | 144 | 0.03 | 0.03 | 1000 | 555 |  |  | 174825 | 4745250 | 0.071229 | 60 | 0.07 | 1.11 |  | CHP costs surcharge estimated based on source [A] by doubling the share of "Turbine Plant Equipment" of total power plant costs.
nucHigh | 1 | Conventional LWR CHP | nuclearLWRchp | [5 empty] | Nuclear | elec | dheat |  |  | 0.9 | 0.9 | 0.8 | 1 | 0.5 | -0.14 | 3.91 |  | 12 | 40 | 1.95 | 35.65 | 3.89 | 690 | 0.98 | 17.83 | 36 | 144 | 0.05 | 0.05 | 1300 | 690 |  |  | 211140 | 8021250 | 0.07062 | 70 | 0.07 | 1.15
nucMax | 1 | Conventional LWR CHP | nuclearLWRchp | [5 empty] | Nuclear | elec | dheat |  |  | 0.94 | 0.94 | 0.95 | 1 | 0.6 | -0.13 | 20.01 |  | 96 | 96 | 1.95 | 122 | 3.89 | 2440 | 0.98 | 61 | 36 | 144 | 0.1 | 0.2 | 1750 | 2440 |  |  | 252540 | 17568000 | 0.070314 | 80 | 0.07 | 1.22
nucMin | 1 | Small Modular LWR | nuclearSMLWR | [5 empty] | Nuclear | elec |  |  |  | 0.23 | 0.23 | 0.15 | 1 |  |  | 1.2 |  | 2 | 2 | 1.95 | 5 | 3.89 | 300 | 0.98 | 2.5 | 36 | 144 | 0.005 | 0.005 | 20 | 300 |  |  | 30000 | 1350000 | 0.075009 | 40 | 0.07 |  | 0.9
nucLow | 1 | Small Modular LWR | nuclearSMLWR | [5 empty] | Nuclear | elec |  |  |  | 0.31 | 0.31 | 0.2 | 1 |  |  | 2.2 |  | 4 | 10 | 1.95 | 11 | 3.89 | 400 | 0.98 | 5.5 | 36 | 144 | 0.01 | 0.01 | 100 | 400 |  |  | 106200 | 1800000 | 0.07246 | 50 | 0.07 |  | 0.9
nucTypical | 1 | Small Modular LWR | nuclearSMLWR | [5 empty] | Nuclear | elec |  |  |  | 0.33 | 0.33 | 0.4 | 1 |  |  | 2.6 |  | 6 | 12 | 1.95 | 21 | 3.89 | 500 | 0.98 | 10.5 | 36 | 144 | 0.03 | 0.03 | 150 | 500 |  |  | 122400 | 4725000 | 0.071229 | 60 | 0.07 |  | 0.9 | Uses 0.9 EUR/USD average conversion rate between 2020-2025
nucHigh | 1 | Small Modular LWR | nuclearSMLWR | [5 empty] | Nuclear | elec |  |  |  | 0.35 | 0.35 | 0.5 | 1 |  |  | 2.8 |  | 48 | 48 | 1.95 | 31 | 3.89 | 600 | 0.98 | 15.5 | 36 | 144 | 0.05 | 0.05 | 200 | 600 |  |  | 194400 | 9000000 | 0.07062 | 70 | 0.07 |  | 0.9
nucMax | 1 | Small Modular LWR | nuclearSMLWR | [5 empty] | Nuclear | elec |  |  |  | 0.42 | 0.42 | 0.95 | 1 |  |  | 16.4 |  | 96 | 96 | 1.95 | 100 | 3.89 | 2000 | 0.98 | 50 | 36 | 144 | 0.1 | 0.2 | 300 | 2000 |  |  | 252000 | 18000000 | 0.070314 | 80 | 0.07 |  | 0.9
nucMin | 1 | Small Modular LWR CHP | nuclearSMLWRchp | [5 empty] | Nuclear | elec | dheat |  |  | 0.81 | 0.81 | 0.15 | 1 | 0.2 | -0.17 | 1.2 |  | 2 | 2 | 1.95 | 5 | 3.89 | 300 | 0.98 | 2.5 | 36 | 144 | 0.005 | 0.005 | 20 | 300 |  |  | 30000 | 1350000 | 0.075009 | 40 | 0.07 | 1
nucLow | 1 | Small Modular LWR CHP | nuclearSMLWRchp | [5 empty] | Nuclear | elec | dheat |  |  | 0.86 | 0.86 | 0.2 | 1 | 0.3 | -0.16 | 2.33 |  | 4 | 10 | 1.95 | 11.66 | 3.89 | 424 | 0.98 | 5.83 | 36 | 144 | 0.01 | 0.01 | 100 | 424 |  |  | 112572 | 1908000 | 0.07246 | 50 | 0.07 | 1.06
nucTypical | 1 | Small Modular LWR CHP | nuclearSMLWRchp | [5 empty] | Nuclear | elec | dheat |  |  | 0.9 | 0.9 | 0.4 | 1 | 0.4 | -0.15 | 2.89 |  | 6 | 12 | 1.95 | 23.31 | 3.89 | 555 | 0.98 | 11.66 | 36 | 144 | 0.03 | 0.03 | 150 | 555 |  |  | 135864 | 5244750 | 0.071229 | 60 | 0.07 | 1.11 |  | CHP costs surcharge estimated based on source [A] by doubling the share of "Turbine Plant Equipment" of total power plant costs.
nucHigh | 1 | Small Modular LWR CHP | nuclearSMLWRchp | [5 empty] | Nuclear | elec | dheat |  |  | 0.93 | 0.93 | 0.5 | 1 | 0.5 | -0.14 | 3.22 |  | 48 | 48 | 1.95 | 35.65 | 3.89 | 690 | 0.98 | 17.83 | 36 | 144 | 0.05 | 0.05 | 200 | 690 |  |  | 223560 | 10350000 | 0.07062 | 70 | 0.07 | 1.15
nucMax | 1 | Small Modular LWR CHP | nuclearSMLWRchp | [5 empty] | Nuclear | elec | dheat |  |  | 0.94 | 0.94 | 0.95 | 1 | 0.6 | -0.13 | 20.01 |  | 96 | 96 | 1.95 | 122 | 3.89 | 2440 | 0.98 | 61 | 36 | 144 | 0.1 | 0.2 | 300 | 2440 |  |  | 307440 | 21960000 | 0.070314 | 80 | 0.07 | 1.22
nucMin | 1 | Small Modular LWR DH | nuclearSMLWRdh | [5 empty] | Nuclear | dheat |  |  |  | 0.81 | 0.81 | 0.15 | 1 |  |  | 0 |  | 2 | 2 | 1.95 | 1 | 3.89 | 50 | 0.98 | 0.5 | 36 | 144 | 0.005 | 0.005 | 20 | 50 |  |  | 7320 | 244000 | 0.075009 | 40 | 0.07
nucLow | 1 | Small Modular LWR DH | nuclearSMLWRdh | [5 empty] | Nuclear | dheat |  |  |  | 0.88 | 0.88 | 0.2 | 1 |  |  | 0.5 |  | 4 | 10 | 1.95 | 5 | 3.89 | 150 | 0.98 | 2.5 | 36 | 144 | 0.01 | 0.01 | 100 | 150 |  |  | 27000 | 489000 | 0.07246 | 50 | 0.07
nucTypical | 1 | Small Modular LWR DH | nuclearSMLWRdh | [5 empty] | Nuclear | dheat |  |  |  | 0.9 | 0.9 | 0.4 | 1 |  |  | 1 |  | 6 | 12 | 1.95 | 11 | 3.89 | 250 | 0.98 | 5.5 | 36 | 144 | 0.03 | 0.03 | 150 | 250 |  |  | 33000 | 978000 | 0.071229 | 60 | 0.07 |  |  | DH reactor startup costs halved due to assumed simplicity compared to CHP reactors.
nucHigh | 1 | Small Modular LWR DH | nuclearSMLWRdh | [5 empty] | Nuclear | dheat |  |  |  | 0.92 | 0.92 | 0.5 | 1 |  |  | 2 |  | 48 | 48 | 1.95 | 21 | 3.89 | 350 | 0.98 | 10.5 | 36 | 144 | 0.05 | 0.05 | 200 | 350 |  |  | 40000 | 1466000 | 0.07062 | 70 | 0.07
nucMax | 1 | Small Modular LWR DH | nuclearSMLWRdh | [5 empty] | Nuclear | dheat |  |  |  | 0.94 | 0.94 | 0.95 | 1 |  |  | 6.3 |  | 96 | 96 | 1.95 | 50 | 3.89 | 1000 | 0.98 | 25 | 36 | 144 | 0.1 | 0.2 | 300 | 1000 |  |  | 67500 | 2250000 | 0.070314 | 80 | 0.07
nucMin | 1 | Micro Modular LWR | nuclearMMLWR | [5 empty] | Nuclear | elec |  |  |  | 0.23 | 0.23 | 0.15 | 1 |  |  | 1.2 |  | 1 | 1 | 1.95 | 5 | 3.89 | 300 | 0.98 | 2.5 | 18 | 72 | 0.005 | 0.005 | 1 | 300 |  |  | 135000 | 3600000 | 0.075009 | 40 | 0.07 |  | 0.9
nucLow | 1 | Micro Modular LWR | nuclearMMLWR | [5 empty] | Nuclear | elec |  |  |  | 0.31 | 0.31 | 0.2 | 1 |  |  | 2.2 |  | 2 | 5 | 1.95 | 11 | 3.89 | 400 | 0.98 | 5.5 | 18 | 72 | 0.01 | 0.01 | 5 | 400 |  |  | 225000 | 9000000 | 0.07246 | 50 | 0.07 |  | 0.9
nucTypical | 1 | Micro Modular LWR | nuclearMMLWR | [5 empty] | Nuclear | elec |  |  |  | 0.33 | 0.33 | 0.4 | 1 |  |  | 2.6 |  | 3 | 6 | 1.95 | 21 | 3.89 | 500 | 0.98 | 10.5 | 18 | 72 | 0.03 | 0.03 | 10 | 500 |  |  | 315000 | 13500000 | 0.071229 | 60 | 0.07 |  | 0.9 | Micro reactor temperatures assumed to stabilise and cool down faster after shutdown due to smaller core size.
nucHigh | 1 | Micro Modular LWR | nuclearMMLWR | [5 empty] | Nuclear | elec |  |  |  | 0.35 | 0.35 | 0.5 | 1 |  |  | 2.8 |  | 24 | 24 | 1.95 | 31 | 3.89 | 600 | 0.98 | 15.5 | 18 | 72 | 0.05 | 0.05 | 15 | 600 |  |  | 405000 | 18000000 | 0.07062 | 70 | 0.07 |  | 0.9
nucMax | 1 | Micro Modular LWR | nuclearMMLWR | [5 empty] | Nuclear | elec |  |  |  | 0.42 | 0.42 | 0.95 | 1 |  |  | 16.4 |  | 48 | 48 | 1.95 | 100 | 3.89 | 2000 | 0.98 | 50 | 18 | 72 | 0.1 | 0.2 | 20 | 2000 |  |  | 550000 | 27000000 | 0.070314 | 80 | 0.07 |  | 0.9
nucMin | 1 | Micro Modular LWR CHP | nuclearMMLWRchp | [5 empty] | Nuclear | elec | dheat |  |  | 0.81 | 0.81 | 0.15 | 1 | 0.2 | -0.17 | 1.2 |  | 1 | 1 | 1.95 | 5 | 3.89 | 300 | 0.98 | 2.5 | 18 | 72 | 0.005 | 0.005 | 1 | 300 |  |  | 135000 | 3600000 | 0.075009 | 40 | 0.07 | 1
nucLow | 1 | Micro Modular LWR CHP | nuclearMMLWRchp | [5 empty] | Nuclear | elec | dheat |  |  | 0.86 | 0.86 | 0.2 | 1 | 0.3 | -0.16 | 2.33 |  | 2 | 5 | 1.95 | 11.66 | 3.89 | 424 | 0.98 | 5.83 | 18 | 72 | 0.01 | 0.01 | 5 | 424 |  |  | 238500 | 9540000 | 0.07246 | 50 | 0.07 | 1.06
nucTypical | 1 | Micro Modular LWR CHP | nuclearMMLWRchp | [5 empty] | Nuclear | elec | dheat |  |  | 0.9 | 0.9 | 0.4 | 1 | 0.4 | -0.15 | 2.89 |  | 3 | 6 | 1.95 | 23.31 | 3.89 | 555 | 0.98 | 11.66 | 18 | 72 | 0.03 | 0.03 | 10 | 555 |  |  | 349650 | 14985000 | 0.071229 | 60 | 0.07 | 1.11 |  | CHP costs surcharge estimated based on source [A] by doubling the share of "Turbine Plant Equipment" of total power plant costs.
nucHigh | 1 | Micro Modular LWR CHP | nuclearMMLWRchp | [5 empty] | Nuclear | elec | dheat |  |  | 0.93 | 0.93 | 0.5 | 1 | 0.5 | -0.14 | 3.22 |  | 24 | 24 | 1.95 | 35.65 | 3.89 | 690 | 0.98 | 17.83 | 18 | 72 | 0.05 | 0.05 | 15 | 690 |  |  | 465750 | 20700000 | 0.07062 | 70 | 0.07 | 1.15
nucMax | 1 | Micro Modular LWR CHP | nuclearMMLWRchp | [5 empty] | Nuclear | elec | dheat |  |  | 0.94 | 0.94 | 0.95 | 1 | 0.6 | -0.13 | 20.01 |  | 48 | 48 | 1.95 | 122 | 3.89 | 2440 | 0.98 | 61 | 18 | 72 | 0.1 | 0.2 | 20 | 2440 |  |  | 671000 | 32940000 | 0.070314 | 80 | 0.07 | 1.22
nucMin | 1 | Micro Modular LWR DH | nuclearMMLWRdh | [5 empty] | Nuclear | dheat |  |  |  | 0.81 | 0.81 | 0.15 | 1 |  |  | 0 |  | 1 | 1 | 1.95 | 1 | 3.89 | 50 | 0.98 | 0.5 | 18 | 72 | 0.005 | 0.005 | 1 | 50 |  |  | 7320 | 244000 | 0.075009 | 40 | 0.07
nucLow | 1 | Micro Modular LWR DH | nuclearMMLWRdh | [5 empty] | Nuclear | dheat |  |  |  | 0.88 | 0.88 | 0.2 | 1 |  |  | 0.5 |  | 2 | 5 | 1.95 | 5 | 3.89 | 150 | 0.98 | 2.5 | 18 | 72 | 0.01 | 0.01 | 10 | 150 |  |  | 27000 | 489000 | 0.07246 | 50 | 0.07
nucTypical | 1 | Micro Modular LWR DH | nuclearMMLWRdh | [5 empty] | Nuclear | dheat |  |  |  | 0.92 | 0.92 | 0.4 | 1 |  |  | 1 |  | 3 | 6 | 1.95 | 11 | 3.89 | 250 | 0.98 | 5.5 | 18 | 72 | 0.03 | 0.03 | 25 | 250 |  |  | 33000 | 978000 | 0.071229 | 60 | 0.07 |  |  | Micro reactor temperatures assumed to stabilise and cool down faster after shutdown due to smaller core size.
nucHigh | 1 | Micro Modular LWR DH | nuclearMMLWRdh | [5 empty] | Nuclear | dheat |  |  |  | 0.94 | 0.94 | 0.5 | 1 |  |  | 2 |  | 24 | 24 | 1.95 | 21 | 3.89 | 350 | 0.98 | 10.5 | 18 | 72 | 0.05 | 0.05 | 40 | 350 |  |  | 40000 | 1466000 | 0.07062 | 70 | 0.07
nucMax | 1 | Micro Modular LWR DH | nuclearMMLWRdh | [5 empty] | Nuclear | dheat |  |  |  | 0.95 | 0.95 | 0.95 | 1 |  |  | 6.3 |  | 48 | 48 | 1.95 | 50 | 3.89 | 1000 | 0.98 | 25 | 18 | 72 | 0.1 | 0.2 | 50 | 1000 |  |  | 67500 | 2250000 | 0.070314 | 80 | 0.07
Note on S1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Roughly guesstimated based on DEA technology data for biomass fired CHP plants, since they seem to operate roughly in similar steam temperature ranges as LWRs.
Note on U1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Note that the variable O&M costs mostly DON’T include the cost of spent nuclear fuel! Although some of the `nucMax` values might.
Note on W1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: `minOperationHours` and `minShutDownHours` mostly based on EUR Document 2.2-2.1.2-C. SMRs are given the benefit of the doubt.
Note on Y1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Warm and Hot startup parameters guesstimated based on the Cold ones by scaling with the relative `minShutDownHours` difference.
Note on AA1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Legacy data? Original source unknown, maybe derived from ERAA24?
Note on AB1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Only two startup cost values found in literature, rest are guesstimated based on legacy data.
Note on AE1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: `startWarmAfterXHours´ mostly based on EUR Document 2.2-2.1.2-C
Note on AF1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: 4x times warm like in ERAA24
Note on AI1: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: The max and min unit sizes in each category are well defined, but the typical reactor sizes within them is somewhat assumed.